## 01_Calc
Humidity_Willim_01.ods				04-Aug-2017			Enter Data in Yellow Cells B5 and C5, or Green Cells, B8, B11 or D5 as required

Enter Temperature (within the range -100 – 373^C) & RH %
	Note For High Temperatures adjust RH% to keep %Mv below 100%						↔ ↔ ↔	NOT logical otherwise
Temp ^C	RH %	m/s	mi/hr	km/hr	knots
33.0	54.9	0.0	0.00	0.00	0.00
		Enter Wind Speed m/s For Australian Apparent Temperature
Wet Bulb	RH %
25.56	54.9	Enter Wet Bulb Temp if RH Unknown and Set Cell C5 '= C8' if many calculations

Altitude	Pressure				http://www.mide.com/pages/air-pressure-at-altitude-calculator
m	hPa - mb	lbf/in2	mm Hg	in Hg
0	1013.25	14.696	760.00	29.921				0.0	'=Temp Change Due to Altitude ^C / ^K
0	1013.25	14.696	760.00	29.921	Pressure at Sea Level T=15^C			33.0	'= Sea Level Equivalent 'Temp'

			Sea Level	Dry	'+'Vapour'					Wind			Enthalpy	Moist Air		Moist Air	Sea Level		Density				Enthalpy	T= 0 - 60
	Vapour	RH %	Temp	MR – HR	SH	AH	%Mv	Td	AAT	Speed	H air	H vap	H air+vap	Density	Energy	Sp Vol	Temp	Air+Vap	Air+Vap	Air	Vap		Air+Vap	Air	Vap
	Over	%	^C	g/kg	g/kg	g/m3	%	^C	^C	m/s			kJ/kg	kg/m3	kJ/m3	m3/kg	^C	m3/kg	kg/m3	kg/m3	kg/m3
	Water	100.0	33.0	32.5268	31.4977	35.6385	4.9696					116.69				33.0
-	Water	54.9	33.0	17.4430	17.1415	19.5625	2.7279	22.66	38.1	0.0	33.3	44.70	78.03	1.141	89.1	0.892	33.0	0.871	1.148	1.122	0.027		77.9	33.2	44.7

33	54.8914267632	22.6647071396	17.4429605531	78.0314238687	33.33	44.7014238687	89.0523795468		← Cells B18-I18 have been set to ease copying and pasting data to another spreadsheet – change as required

				54.8914267632	25.56	19.5624784092	22.6647071396

	Convert										Heat Index	Lower Temp	Upper RH	Heat Index
	^C → ^F											Valid	Valid	37.6		Valid T >= 26.6 and RH >=40
^C	33.0	22.7	25.6	38.1	0.0	100.0	^C				Valid	Valid	Valid	39.1		Valid T = 21.1 – 46.1 and RH 0 – 80 if Heat Index < 65.6
^F	91.4	72.8	78.0	100.5	32.0	212.0	^F					Valid		38.6		Appears to be Valid for T>=26.6 - Other Constraints Unknown
	T	Td	Tw	AAT								AAT
												38.1
	Convert
	^F → ^C
^F	32.0	50.0	68.0	86.0	104.0	212.0	^F
^C	0.0	10.0	20.0	30.0	40.0	100.0	^C

## 02_Comfort
Now		06-Aug-2017 13:06
Modified		04-Aug-2017 06:00
				RH %					RH %
		NOTE		25	25	30	30	35	35	40	40	45	45	50	50	55	55	60	60	65	65	70	70		75	75	80	80	85	85	90	90	100	100
		There is contradictory information on the links
		Choose what best suits one's needs …		AH	Td	AH	Td	AH	Td	AH	Td	AH	Td	AH	Td	AH	Td	AH	Td	AH	Td	AH	Td		AH	Td	AH	Td	AH	Td	AH	Td	AH	Td
				g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C		g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C	g/m3	^C
			T ^C
		“High Normal” Body Temperature	37.8					Mould
		“Normal” Body Temperature	37					Mould
		“Low Normal” Body Temperature	36.1					Mould
			36	10.4	12.9	12.5	15.7	14.6	18.1	16.7	20.2	18.8	22.1	20.9	23.9	23.0	25.5	25.0	26.9	27.1	28.3	29.2	29.6		31.3	30.8	33.4	31.9	35.5	33.0	37.6	34.0	41.7	36
		http://www.bbc.com/news/science-environment-40793019 Skin Temp	35	9.9	12.0	11.9	14.8	13.9	17.2	15.8	19.3	17.8	21.2	19.8	23.0	21.8	24.5	23.8	26.0	25.8	27.4	27.7	28.6		29.7	29.8	31.7	31.0	33.7	32.0	35.7	33.0	39.6	35
		http://dpcalc.org/index.php “Days to mould”	35					← NO Risk -	157			37		13		6		4		2	35
			34	9.4	11.2	11.3	14.0	13.2	16.3	15.0	18.4	16.9	20.3	18.8	22.1	20.7	23.6	22.6	25.1	24.4	26.4	26.3	27.7		28.2	28.9	30.1	30.0	32.0	31.1	33.8	32.1	37.6	34
			33	8.9	10.4	10.7	13.1	12.5	15.5	14.3	17.6	16.0	19.4	17.8	21.1	19.6	22.7	21.4	24.1	23.2	25.5	24.9	26.7		26.7	27.9	28.5	29.0	30.3	30.1	32.1	31.1	35.6	33
			32	8.5	9.5	10.1	12.2	11.8	14.6	13.5	16.7	15.2	18.5	16.9	20.2	18.6	21.8	20.3	23.2	22.0	24.5	23.7	25.8		25.4	26.9	27.1	28.0	28.8	29.1	30.4	30.1	33.8	32
			31	8.0	8.7	9.6	11.4	11.2	13.7	12.8	15.8	14.4	17.6	16.0	19.3	17.6	20.8	19.2	22.3	20.8	23.6	22.4	24.8		24.0	26.0	25.6	27.1	27.2	28.1	28.8	29.1	32.0	31
		Panasonic Split Upper Temperature	30	7.6	7.8	9.1	10.5	10.6	12.9	12.2	14.9	13.7	16.7	15.2	18.4	16.7	19.9	18.2	21.3	19.8	22.6	21.3	23.9		22.8	25.0	24.3	26.1	25.8	27.1	27.3	28.1	30.4	30
			29	7.2	7.0	8.6	9.7	10.1	12.0	11.5	14.0	12.9	15.8	14.4	17.5	15.8	19.0	17.3	20.4	18.7	21.7	20.1	22.9		21.6	24.1	23.0	25.1	24.4	26.2	25.9	27.1	28.8	29
			28	6.8	6.2	8.2	8.8	9.5	11.1	10.9	13.1	12.3	14.9	13.6	16.6	15.0	18.1	16.3	19.5	17.7	20.8	19.1	22.0		20.4	23.1	21.8	24.2	23.2	25.2	24.5	26.1	27.2	28
			27	6.4	5.3	7.7	8.0	9.0	10.2	10.3	12.2	11.6	14.0	12.9	15.7	14.2	17.2	15.5	18.5	16.8	19.8	18.0	21.0		19.3	22.1	20.6	23.2	21.9	24.2	23.2	25.2	25.8	27
			26	6.1	4.5	7.3	7.1	8.5	9.4	9.8	11.3	11.0	13.1	12.2	14.7	13.4	16.2	14.6	17.6	15.9	18.9	17.1	20.1		18.3	21.2	19.5	22.2	20.7	23.2	22.0	24.2	24.4	26
			25	5.8	3.6	6.9	6.2	8.1	8.5	9.2	10.5	10.4	12.2	11.5	13.8	12.7	15.3	13.8	16.7	15.0	17.9	16.1	19.1		17.3	20.2	18.4	21.3	19.6	22.2	20.7	23.2	23.0	25
			24	5.4	2.8	6.5	5.4	7.6	7.6	8.7	9.6	9.8	11.3	10.9	12.9	12.0	14.4	13.1	15.7	14.2	17.0	15.2	18.1		16.3	19.2	17.4	20.3	18.5	21.3	19.6	22.2	21.8	24
			23	5.1	2.0	6.2	4.5	7.2	6.7	8.2	8.7	9.3	10.4	10.3	12.0	11.3	13.5	12.3	14.8	13.4	16.0	14.4	17.2		15.4	18.3	16.5	19.3	17.5	20.3	18.5	21.2	20.6	23
			22	4.9	1.1	5.8	3.7	6.8	5.9	7.8	7.8	8.7	9.5	9.7	11.1	10.7	12.5	11.7	13.9	12.6	15.1	13.6	16.2		14.6	17.3	15.5	18.3	16.5	19.3	17.5	20.2	19.4	22
			21	4.6	0.3	5.5	2.8	6.4	5.0	7.3	6.9	8.2	8.6	9.2	10.2	10.1	11.6	11.0	12.9	11.9	14.1	12.8	15.3		13.7	16.4	14.7	17.4	15.6	18.3	16.5	19.2	18.3	21
			20	4.3	-0.6	5.2	2.0	6.1	4.1	6.9	6.0	7.8	7.7	8.6	9.3	9.5	10.7	10.4	12.0	11.2	13.2	12.1	14.3		13.0	15.4	13.8	16.4	14.7	17.4	15.6	18.3	17.3	20
		http://dpcalc.org/index.php “Days to mould”	20					← NO Risk -	157			38		14		6		4		2	20
			19	4.1	-1.4	4.9	1.1	5.7	3.2	6.5	5.1	7.3	6.8	8.2	8.3	9.0	9.8	9.8	11.0	10.6	12.3	11.4	13.4		12.2	14.4	13.0	15.4	13.9	16.4	14.7	17.3	16.3	19
			18	3.8	-2.2	4.6	0.2	5.4	2.4	6.1	4.2	6.9	5.9	7.7	7.4	8.5	8.8	9.2	10.1	10.0	11.3	10.8	12.4		11.5	13.5	12.3	14.5	13.1	15.4	13.8	16.3	15.4	18
			17	3.6	-3.1	4.3	-0.6	5.1	1.5	5.8	3.3	6.5	5.0	7.2	6.5	8.0	7.9	8.7	9.2	9.4	10.4	10.1	11.5		10.9	12.5	11.6	13.5	12.3	14.4	13.0	15.3	14.5	17
		Panasonic Split Lower Temperature	16	3.4	-3.9	4.1	-1.5	4.8	0.6	5.5	2.5	6.1	4.1	6.8	5.6	7.5	7.0	8.2	8.2	8.9	9.4	7.9	10.5		10.2	11.6	10.9	12.5	11.6	13.4	12.3	14.3	13.6	16
		http://dpcalc.org/index.php “Days to mould”	16					← NO Risk -		42		15		7		4		2	16
							Mould
					Possible Comfort – Anti Mould Envelope for Philippines					Mould
					RH 30-60% T 20-36^C for Cebu, Philippines					Mould
							Mould
		Most people can not sense RH variation in this range –
		Hence defined as “comfort range”
		From Building Science Corporation
		RR-0203: Relative Humidity Joseph Lstiburek 23-Apr-2002

		Air too dry – may have issues with nosebleeds and static electricity

		https://en.wikipedia.org/wiki/Relative_humidity

		RH less than 45% prone to static
		''https://www.herrmidifier-hvac.com/getfile2.aspx?fileid=9004
		Page 6 ….

		RH 50%+ = Reduced Dust mites & less damage to fabrics etc e.g. carpets, curtains etc.
		''https://www.herrmidifier-hvac.com/getfile2.aspx?fileid=9004
		50% appears to be a good target

		'' http://www.sensitivechoice.com/indoor-humidity/
		RH less than 60% - Effective in reducing dust mites

		''http://www.humiditycontrol.co.uk/humidity.htm
		Air in PI will condense in cold spots and may cause mould
		Minimum Dew Point 20^C – only 6 days 1998 – 2016 less than 20^C

		RH 70%+ = mould etc .. at coldest surface in area

		Relative Humidity %		RH
		Specific Humidity grammes water vapour per kilogramme of air g/kg		SH
		Dew Point Temperature ^C		Td
		Moisture Vapour %		% Mv

	RH	At T 32^C and 1013mb			SH	AH	% Mv	Td
					g/kg	g/m3	%	^C
	90.0				26.7	30.4	4.2	30	30
		Severely High – Even deadly for asthma related illnesses
	70.9				21.0	24.0	3.3	25.9921898455	26
70		Mould !! - if 70 or greater			20.7	23.7	3.3	25.8
		Extremely uncomfortable, fairly oppressive
	63.0				18.6	21.3	3.0	24	24
		Very Humid quite uncomfortable
	52.4				15.5	17.7	2.5	21	21
		Somewhat uncomfortable for most people at upper edge
	43.5				12.8	14.7	2.0	18	18
		OK for most but all perceive humidity at upper edge
	38.2				11.2	12.9	1.8	16	16
		Comfortable
	31.5				9.3	10.6	1.5	13	13
	29.6				8.7	10.0	1.4	12	12
		Very Comfortable
	25.8				7.6	8.7	1.2	10	10
		A bit dry for some
	14.8				4.3	5.0	0.7	2	2

		Above based on “High Dew Points Uncomfortable”

		Page 12 of WaterVapor.pdf Jim Washburne Sep., 2010

		''http://web.sahra.arizona.edu/education2/fossww/PCL/WaterVapor.pdf
		''https://en.wikipedia.org/wiki/Dew_point					Same data – better table, more logical

		''http://www.lenntech.com/calculators/humidity/relative-humidity.htm

		''http://web.gccaz.edu/~lnewman/gph111/topic_units/Labs_all/Water%20Vapor%20Capacity%20of%20Air.pdf

		''https://buildingscience.com/documents/reports/rr-0203-relative-humidity/view

		'' https://www.timeanddate.com/weather/philippines/cebu-city/historic?month=1&year=2016

				“Hermidifier Comfort Guide – ex Table 1B
							SH	AH	% Mv	Td
						^F	RH		^C		g/kg	g/m3	%	^C

				Factory		78	10		25.6		2.0	2.4	0.3	-8.1
						72	20		22.2		3.3	3.9	0.5	-1.7
						68	30		20.0		4.3	5.2	0.7	2.0
						65	40		18.3		5.2	6.3	0.8	4.5

				Office		79	20		26.1		4.2	4.9	0.7	1.4
						76	25		24.4		4.7	5.6	0.8	3.1
						70	30		21.1		4.6	5.5	0.7	2.9
						68	45		20.0		6.5	7.8	1.0	7.7

							All seem to be “dry” to me as Td < 8^C

## 03_Wet_Bulb
http://web.sahra.arizona.edu/education2/fossww/PCL/WaterVapor.pdf					Wet Bulb Depression = Dry Bulb – Wet Bulb Temperature ^C
...Arizona.edu/..		1		2		3		4		5		6		7		8		9		10		11		12		13		14		15		16		17		18		19		20		21		22
Willim			1		2		3		4		5		6		7		8		9		10		11		12		13		14		15		16		17		18		19		20		21		22		23		24		25
	-20	28	39.6
	-18	40	47.9					''http://www.1728.org/relhum.htm
	-16	48	54.7	0	10.1					N=	0.6687451584
	-14	55	60.5	11	21.5					Dry Bulb					Wet Bulb
	-12	61	65.3	23	31.1
	-10	66	69.3	33	39.2	0	9.7					Relative Humidity Values					T	-10		ed=	2.864785		Tw	-35		ew=	0.3122909972		RH	-549.20
	-8	71	72.7	41	46.0	13	19.9					T	-8		ed=	3.3509692445		Tw	-33		ew=	0.3802576934		RH	-468.64
	-6	73	75.6	48	51.8	20	28.5	0	5.6					T	-6		ed=	3.9092182745		Tw	-31		ew=	0.4612829444		RH	-400.63
	-4	77	78.1	54	56.7	32	35.8	11	15.4					T	-4		ed=	4.5486216392		Tw	-29		ew=	0.5575370619		RH	-343.04
Dry Bulb	-2	79	80.2	58	60.9	37	42.1	20	23.7	1	5.8					T	-2		ed=	5.2792044519		Tw	-27		ew=	0.6714929154		RH	-294.14
(Air)	0	81	82.0	63	64.5	45	47.5	28	30.9	11	14.6					T	0		ed=	6.112		Tw	-25		ew=	0.8059595063		RH	-252.49
Temperature	2	83	83.6	67	67.6	51	52.1	36	37.0	20	22.2	6	7.9					T	2		ed=	7.0591258083		Tw	-23		ew=	0.9641181991		RH	-216.92
	4	85	84.9	70	70.3	56	56.1	42	42.3	27	28.8	14	15.7		2.9					T	4		ed=	8.1338631617		Tw	-21		ew=	1.1495617134		RH	-186.45
^C	6	86	86.1	72	72.6	59	59.5	46	46.8	35	34.5	22	22.5	10	10.8	0					T	6		ed=	9.3507400821		Tw	-19		ew=	1.3663359721		RH	-160.28
	8	87	87.1	74	74.6	62	62.5	51	50.8	39	39.4	28	28.3	17	17.6	6	7.1					T	8		ed=	10.7256177436		Tw	-17		ew=	1.6189849003		RH	-137.73
	10	88	88.0	76	76.4	65	65.1	54	54.2	43	43.7	33	33.4	24	23.5	13	13.8	4	4.4					T	10		ed=	12.2757803015		Tw	-15		ew=	1.9125982609		RH	-118.26
	12	88	88.8	78	77.9	67	67.4	57	57.2	48	47.4	38	37.9	28	28.6	19	19.7	10	11.0	2	2.5					T	12		ed=	14.0200280988		Tw	-13		ew=	2.2528626052		RH	-101.40
	14	89	89.4	79	79.3	69	69.4	60	59.9	50	50.7	41	41.8	33	33.2	25	24.8	16	16.7	8	8.9	1	1.2					T	14		ed=	15.9787742027		Tw	-11		ew=	2.6461154139		RH	-86.75
	16	90	90.0	80	80.4	71	71.2	62	62.2	54	53.6	45	45.2	37	37.1	29	29.3	21	21.7	14	14.4	7	7.3	1	0.4					T	16		ed=	18.1741442172		Tw	-9		ew=	3.0994024902		RH	-73.99
	18	91	90.6	81	81.5	72	72.7	64	64.3	56	56.1	48	48.2	40	40.6	33	33.3	26	26.2	19	19.3	12	12.6	6	6.2	0					T	18		ed=	20.6300793023		Tw	-7		ew=	3.6205386644		RH	-62.84
	20	91	91.0	82	82.4	74	74.1	66	66.1	58	58.4	51	50.9	44	43.7	36	36.8	30	30.1	23	23.6	17	17.3	11	11.2	5	5.4					T	20		ed=	23.372442326		Tw	-5		ew=	4.2181718568		RH	-53.07
	22	92	91.5	83	83.3	75	75.3	68	67.7	60	60.4	53	53.3	46	46.5	40	39.9	33	33.5	27	27.4	21	21.5	15	15.7	10	10.2	4	4.8	0					T	22		ed=	26.42912706		Tw	-3		ew=	4.9018505376		RH	-44.49
	24	92	91.8	84	84.0	76	76.4	69	69.2	62	62.2	55	55.4	49	48.9	42	42.7	36	36.6	30	30.8	25	25.2	20	19.7	14	14.5	9	9.4	4	4.5	0					T	24		ed=	29.8301703267		Tw	-1		ew=	5.6820946156		RH	-36.93
	26	92	92.2	85	84.7	77	77.4	70	70.5	64	63.8	57	57.3	51	51.1	45	45.1	39	39.4	34	33.8	28	28.5	23	23.3	18	18.3	13	13.5	9	8.8	5	4.3					T	26		ed=	33.6078669892		Tw	1		ew=	6.5704697725		RH	-30.25
	28	93	92.5	86	85.3	78	78.3	71	71.6	65	65.2	59	59.0	53	53.1	45	47.4	42	41.8	36	36.5	31	31.4	26	26.5	21	21.7	17	17.1	12	12.7	8	8.4	4	4.2594124558		0.3					T	28		ed=	37.7968876742		Tw	3		ew=	7.5796652568		RH	-24.33
	30	93	92.8	86	85.8	79	79.1	72	72.7	66	66.5	61	60.6	55	54.9	49	49.4	44	44.1	39	39.0	34	34.0	29	29.3	25	24.8	20	20.4	16	16.1	12	12.0	8	8.0892345346	4	4.3		0.6					T	30		ed=	42.4343991022		Tw	5		ew=	8.7235751345		RH	-19.07
	32	93	93.0	86	86.3	80	79.9	73	73.7	68	67.7	62	62.0	56	56.5	51	51.2	46	46.1	41	41.2	36	36.4	32	31.9	27	27.5	22	23.3	19	19.2	14	15.3	11	11.5236121357	8	7.9	4	4.4		1.0					T	32		ed=	47.5601868972		Tw	7		ew=	10.0173829875		RH	-14.37
	34	93	93.3	86	86.8	81	80.5	74	74.5	69	68.8	63	63.2	58	57.9	52	52.8	48	47.9	43	43.1	38	38.6	34	34.2	30	30.0	26	25.9	22	22.0	18	18.2	14	14.6138976234	11	11.1	8	7.7	5	4.5		1.3					T	34		ed=	53.2167807379		Tw	9		ew=	11.4776500399		RH	-10.17
	36	94	93.5	87	87.2	81	81.1	75	75.3	69	69.8	64	64.4	59	59.2	54	54.3	50	49.5	44	44.9	40	40.5	36	36.3	32	32.2	28	28.3	24	24.5	21	20.9	17	17.4041422699	13	14.0	10	10.8	7	7.7	4	4.6		1.7					T	36		ed=	59.4495817039		Tw	11		ew=	13.1224066806		RH	-6.40
	38	94	93.7	87	87.6	82	81.7	76	76.1	70	70.7	66	65.5	60	60.5	55	55.7	51	51.0	46	46.6	42	42.3	38	38.2	34	34.3	30	30.5	26	26.8	23	23.3	20	19.9322083385	16	16.7	13	13.5	10	10.5	7	7.6	5	4.8		2.1					T	38		ed=	66.3069916662		Tw	13		ew=	14.9712473415		RH	-3.01
	40	94	93.8	89	87.9	82	82.2	76	76.7	71	71.5	67	66.4	61	61.6	57	56.9	52	52.4	48	48.1	44	44.0	40	40.0	36	36.1	33	32.5	29	28.9	25	25.5	22	22.2307011421	19	19.1	16	16.0	13	13.1	10	10.3	7	7.6		5.0		2.5		0.1			T	40		ed=	73.8405445645		Tw	15		ew=	17.0454286796		RH	0.05

				T	-20		ed=	1.2537607218		Tw	-22		ew=	1.0531876157		RH	-19.98
				T	-18		ed=	1.4878713671		Tw	-20		ew=	1.2537607218		RH	-3.56
				T	-16		ed=	1.760330223		Tw	-18		ew=	1.4878713671		RH	10.12
				T	-14		ed=	2.0765188802		Tw	-16		ew=	1.760330223		RH	21.55
				T	-12		ed=	2.4424423852		Tw	-14		ew=	2.0765188802		RH	31.14

## 04_ASHRAE
				AH	from Calc_01 Sheet
^F	Grains/ft3	lb/ft3	kg/m3	g/m3	^C		Ratio		g/m3
0	0.475	0.000068	0.0011	1.088	-17.78		1.01		1.082	Over
5	0.609	0.000087	0.0014	1.395	-15.00		1.01		1.387	Ice
10	0.776	0.000111	0.0018	1.777	-12.22		1.00		1.769
15	0.984	0.000141	0.0023	2.253	-9.44		1.00		2.244
20	1.242	0.000177	0.0028	2.844	-6.67		1.01		2.830
25	1.558	0.000223	0.0036	3.568	-3.89		1.00		3.553
30	1.946	0.000278	0.0045	4.456	-1.11		1.00		4.441
35	2.376	0.000339	0.0054	5.441	1.67		1.00		5.436	Over
40	2.863	0.000409	0.0066	6.556	4.44		1.00		6.549	Water
45	3.436	0.000491	0.0079	7.869	7.22		1.00		7.862
50	4.106	0.000587	0.0094	9.403	10.00		1.00		9.398
55	4.889	0.000698	0.0112	11.196	12.78		1.00		11.189
60	5.795	0.000828	0.0133	13.271	15.56		1.00		13.270
65	6.845	0.000978	0.0157	15.675	18.33		1.00		15.669
70	8.055	0.001151	0.0184	18.446	21.11		1.00		18.445
75	9.448	0.001350	0.0216	21.636	23.89		1.00		21.636
80	11.04	0.001577	0.0253	25.282	26.67		1.00		25.291
85	12.87	0.001839	0.0295	29.473	29.44		1.00		29.447
90	14.94	0.002134	0.0342	34.213	32.22		1.00		34.194
95	17.28	0.002469	0.0396	39.572	35.00		1.00		39.581
100	19.95	0.002850	0.0457	45.686	37.78		1.00		45.676
105	22.95	0.003279	0.0526	52.556	40.56		1.00		52.552
110	26.34	0.003763	0.0603	60.319	43.33		1.00		60.257
115	30.13	0.004304	0.0690	68.998	46.11		1.00		68.932

		1	16.0328586916				All Values within 1%

ex- Hermidifier Table 1A ex – ASHRAE Handbook

115	30.13	0.004304	0.0690	68.998	46.11		1.00		68.932	Over
120	34.38	0.004911	0.0787	78.731	48.89		1.00		78.640	Water
125	39.13	0.005590	0.0896	89.608	51.67		1.00		89.476
130	44.41	0.006344	0.1017	101.700	54.44		1.00		101.495
135	50.30	0.007186	0.1152	115.188	57.22		1.00		115.036
140	56.81	0.008116	0.1301	130.096	60.00		1.00		129.737
145	64.04	0.009149	0.1467	146.653	62.78		1.00		146.150
150	72.00	0.010286	0.1649	164.881	65.56		1.00		164.258
155	80.77	0.011539	0.1850	184.965	68.33		1.00		184.117
160	90.43	0.012919	0.2071	207.087	71.11		1.01		206.009
165	101.00	0.014429	0.2313	231.292	73.89		1.01		230.010
170	112.60	0.016086	0.2579	257.856	76.67		1.01		256.271
175	125.40	0.017914	0.2872	287.168	79.44		1.01		284.842
180	139.20	0.019886	0.3188	318.771	82.22		1.01		316.095
185	154.30	0.022043	0.3534	353.350	85.00		1.01		350.099
190	170.70	0.024386	0.3909	390.906	87.78		1.01		387.034
195	188.60	0.026943	0.4319	431.898	90.56		1.01		427.082

		453.923	g=1lb				All Values within 1%

ex- Hermidifier Table 2A ex – ASHRAE Handbook?

## 05_MAC_Inst
1	Data From:-		Machine Applications Corporation					Values ex- 01_Calc					01_Calc Input Values
2		http://www.macinstruments.com/pdf/handbook.pdf
3	% Mv	Td Temp	SH	AH	Hum Ratio					% Mv	Td Temp	SH	AH	Hum Ratio		T	T	RH
4	%	^F	g/kg	g/m3	kg/kg		^F	^C		%	^C	g/kg	g/m3	g/kg		^F	^C	%
5	0	-459.67	0.00	0.00	0		-459.67	-273.15
6	0.1	-4	0.622	0.76	0.000623		-4	-20.00		0.10	-20.09	0.628	0.88	0.629		-4.17	-20.10	100		Over Ice
7	0.2	10	1.24	1.52	0.00125		10	-12.22		0.20	-14.06	1.25	1.70	1.249		6.30	-14.28	100
8	0.3	18	1.87	2.29	0.00187		18	-7.78		0.30	-9.08	1.87	2.50	1.88		15.40	-9.22	100
9	0.4	24	2.49	3.05	0.00250		24	-4.44		0.40	-4.90	2.49	3.27	2.50		23.19	-4.89	100
10	0.5	28	3.12	3.81	0.00313		28	-2.22		0.50	-2.24	3.12	4.06	3.13		27.97	-2.24	100
11	0.6	32	3.74	4.57	0.00375		32	0.00		0.60	0.00	3.74	4.83	3.76		31.90	-0.06	100		Over Water
12	0.7	36	4.37	5.33	0.00438		36	2.22		0.70	2.12	4.37	5.59	4.39		35.75	2.08	100
13	0.8	39	4.99	6.10	0.00502		39	3.89		0.80	3.99	5.00	6.35	5.02		39.00	3.89	100
14	0.9	42	5.62	6.86	0.00565		42	5.56		0.90	5.56	5.59	7.05	5.62		42.00	5.56	100
15	1	45	6.24	7.62	0.00628		45	7.22		1	7.22	6.27	7.86	6.31		45.00	7.22	100
16	2	64	12.5	15.24	0.0127		64	17.78
17	3	76	18.9	22.86	0.0192		76	24.44
18	4	85	25.3	30.48	0.0259		85	29.44
19	5	92	31.7	38.10	0.0327		92	33.33
20	6	98	38.2	45.72	0.0397		98	36.67
21	7	103	44.7	53.33	0.0468		103	39.44
22	8	107	51.3	60.95	0.0541		107	41.67
23	9	111	57.9	68.57	0.0615		111	43.89
24	10	115	64.6	76.19	0.0691		115	46.11		10	46.06	64.80	68.94	69.30		115.00	46.11	100
25	11	118	71.4	83.81	0.0769		118	47.78
26	12	121	78.2	91.43	0.0848		121	49.44
27	13	124	85.0	99.05	0.0929		124	51.11
28	14	127	91.9	106.67	0.101		127	52.78
29	15	130	98.9	114.29	0.110		130	54.44
30	16	132	106	121.91	0.118		132	55.56
31	17	134	113	129.53	0.127		134	56.67
32	18	136	120	137.15	0.137		136	57.78
33	19	139	127	144.77	0.146		139	59.44
34	20	141	135	152.38	0.155		141	60.56		20	60.33	135	131.68	155.52		140.62	60.34	100
35	21	143	142	160.00	0.165		143	61.67
36	22	144	149	167.62	0.175		144	62.22
37	23	146	157	175.24	0.186		146	63.33
38	24	148	164	182.86	0.196		148	64.44
39	25	150	172	190.48	0.207		150	65.56
40	26	151	179	198.10	0.219		151	66.11
41	29	156	203	220.96	0.254		156	68.89
42	30	157	210	228.58	0.267		157	69.44		30	69.46	211	192.65	267.35		157.00	69.44	100
43	31	158	218	236.20	0.279		158	70.00
44	32	160	226	243.82	0.293		160	71.11		32	70.92	227	204.28	292.87		159.62	70.90	100
45	33	161	235	251.43	0.306		161	71.67
46	35	163	251	266.67	0.335		163	72.78
47	36	165	259	274.29	0.350		165	73.89
48	38	167	276	289.53	0.381		167	75.00
49	40	169	293	304.77	0.415		169	76.11		40	76.26	294	251.88	416.08		169.20	76.22	100
50	42	171	311	320.01	0.450		171	77.22
51	45	174	337	342.87	0.509		174	78.89
52	47	176	355	358.10	0.552		176	80.00
53	49	178	374	373.34	0.598		178	81.11
54	50	179	383	380.96	0.622		179	81.67		50	81.72	384	309.66	623.10		179.00	81.67	100
55	51	180	393	388.58	0.647		180	82.22
56	52	181	403	396.20	0.674		181	82.78
57	55	183	432	419.06	0.760		183	83.89
58	57	185	452	434.30	0.824		185	85.00
59	58	186	462	441.92	0.859		186	85.56		58	85.48	463	355.44	860.73		185.75	85.42	100
60	59	187	472	449.53	0.895		187	86.11		59	85.90	472	360.86	895.17		186.50	85.83	100			This area is confusing to me in the MAC Instruments
61	60	187	483	457.15	0.933		187	86.11		60	86.34	483	366.70	934.27		187.30	86.28	100			handbook “duplicate” temperatures are shown with different moisture contents
62	61	188	493	464.77	0.973		188	86.67		61	86.79	494	372.62	976.06		188.10	86.72	100
63	62	189	504	472.39	1.01		189	87.22		62	87.18	504	377.87	1015.04		188.80	87.11	100				“Solved” using 01_Calc
64	63	190	514	480.01	1.06		190	87.78		63	87.59	514	383.56	1059.57		189.55	87.53	100				The issue is rounding errors
65	64	190	525	487.63	1.11		190	87.78		64	88.01	525	389.31	1107.24		190.30	87.94	100				in the temperatures shown
66	65	191	536	495.25	1.16		191	88.33		65	88.41	536	394.83	1155.56		191.01	88.34	100
67	66	192	547	502.87	1.21		192	88.89		66	88.82	548	400.72	1210.37		191.76	88.76	100
68	67	192	558	510.49	1.26		192	88.89		67	89.20	558	406.05	1262.94		192.43	89.13	100
69	68	193	569	518.11	1.32		193	89.44		68	89.59	569	411.68	1321.92		193.13	89.52	100
70	69	194	581	525.30	1.38		194	90.00		69	89.98	581	417.36	1385.52		193.83	89.91	100
71	70	194	592	533.35	1.45		194	90.00		70	90.36	592	423.03	1453.27		194.52	90.29	100
72	71	195	604	540.97	1.52		195	90.56		71	90.73	604	428.52	1523.35		195.18	90.66	100
73	74	197	639	563.83	1.77		197	91.67		74	91.83	639	445.31	1771.50		197.16	91.76	100
74	77	199	676	586.68	2.08		199	92.78		77	92.90	676	462.01	2083.78		199.07	92.82	100
75	80	201	713	609.54	2.49		201	93.89		80	93.93	713	478.67	2490.03		200.92	93.84	100
76	81	201	726	617.16	2.65		201	93.89		81	94.26	726	484.18	2652.87		201.52	94.18	100
77	83	203	752	632.40	3.04		203	95.00		83	94.92	752	495.25	3038.64		202.71	94.84	100
78	88	206	820	670.49	4.56		206	96.67		88	96.52	820	522.89	4571.34		205.59	96.44	100
79	90	207	848	685.73	5.6		207	97.22		90	97.14	849	533.87	5611.61		206.70	97.06	100
80	92	208	877	700.97	7.15		208	97.78		92	97.75	878	544.94	7191.61		207.80	97.67	100
81	96	210	937	731.45	14.9		210	98.89		96	98.93	937	566.69	14986.06		209.91	98.84	100
82	97	210	953	739.07	20.1		210	98.89		97	99.22	953	572.26	20359.43		210.44	99.13	100				This area is confusing to me in the MAC Instruments
83	98	211	968	746.68	30.5		211	99.44		98	99.50	968	577.55	30579.72		210.94	99.41	100				handbook “duplicate” temperatures are shown with different moisture contents
84	99	211	984	754.30	61.6		211	99.44		99	99.79	984	582.99	61907.35		211.45	99.69	100
85	100	212	1000	761.92	infinity		212	100.00		100	100.09	1001	588.91	-678335.94		212.00	100.00	100

## 06_Temp_RH_Td
				Air Temp
	0	5	10	15	20	21	22	23	24	25	26	27	28	29	30
Td					Relative Humidity – RH %
0	100	70	50	36	27	25	24	22	21	20	19	18	17	16	15
5		100	71	52	38	36	33	31	30	28	26	25	24	22	21
10			100	72	53	50	47	44	42	39	37	35	33	31	29
15				100	73	69	65	61	57	54	51	48	45	43	41
20					100	94	88	83	78	74	68	65	62	58	55
21					100	94	89	84	79	74	70	66	62	59
22					100	94	89	84	79	74	70	66	63
23					100	94	89	84	79	75	70	66
24					100	94	89	84	79	75	71
25					100	94	89	84	79	75

## Calc_1
			Sea Level	Dry	'+'Vapour'					Wind			Enthalpy	Moist Air		Moist Air	Sea Level		Density			Enthalpy	T= 0 - 60
	Vapour	RH %	Temp	MR – HR	SH	AH	%Mv	Td	AAT	Speed	H air	H vap	H air+vap	Density	Energy	Sp Vol	Temp	Air+Vap	Air+Vap	Air	Vap	Air+Vap	Air	Vap
	Over	%	^C	g/kg	g/kg	g/m3	%	^C	^C	m/s			kJ/kg	kg/m3	kJ/m3	m3/kg	^C	m3/kg	kg/m3	kg/m3	kg/m3
	Water	100	33.0	32.527	31.498	35.638	4.969586						116.69				33.0
-	Water	54.8914267632	33.0	17.443	17.141	19.562	2.727876	22.66	38.1	0.0	33.33	44.70	78.03	1.141	89.1	0.892	33.0	0.871	1.148	1.1215	0.0267	77.89	33.21	44.68
						Valid >-46	Valid<61	22.7
	Ice	100	Water	45.338	43.365	48.721	6.793908						149.52				Water
-	Ice	54.8914267632	Water	24.094	23.524	26.744	3.729273	24.0	38.1	0.0	33.33	61.75	95.08	1.137	108.1	0.901	Water	0.901	1.110	1.1100	0.0000	81.34	33.17	48.17
							f(T,RH)=	1.5		''https://www.omnicalculator.com/physics/dew-point
Alternative Calculator			http://forms.vaisala.com/LP=1244									Humidity Ratio
	'www.vaisala.com/Vaisala Documents/Application notes/Humidity_Conversion_Formulas_B210973EN-F.pdf											Mix Ratio		Enthalpy
					Range						Td	X	AH	h		h air	h vap
	RH=100%	54.8914267632			Tmin ^C	Tmax ^C		Pw/A	log10(Pw/A)		^C	g/kg	g/m3	kJ/kg
Pws wat	50.4	27.640209			0	373		4.5389105394	0.656951623		22.6647071396	17.443	19.562	78.03142		33.33	44.7014238687
Pws ice	68.8	37.786858			-100	0.01		6.1796324009	0.7909626416		24.0381510268	24.0943	26.744	95.07687		33.33	61.7468723481
							Using equations 3, 4 & 5			'B=	621.9907	'C=	2.16679

												RH=100	RH=100
		Ptot	1013.25	'hPa - mb								32.527	35.638	116.6871028276
	Normal Sea Level Pressure		1013.25	'hPa - mb								45.338	48.721	149.5177647622

T	306.15	^K		0	373								Alt Enthalpy Variables	44.7529039772
Tc	647.096	^K					Mide Equation (2)						Alt Enthalpy Variables	83.4244209766
Pc	220640									Australian Apparent Temperature
n	0.5268862734						Lb K/m	-0.0065		e=	27.5117899668	hPa
c1	-7.85951783		-4.1410720605				R	8.31432		AAT=	38.1	^C
c2	1.84408259		0.7052704605				g m/s2	9.80665			''https://en.wikipedia.org/wiki/Wind_chill
c3	-11.7866497		-1.7240149582				M kg/mol	0.0289644
c4	22.6807411		2.4080546369							-89.2 Lowest Temp Recorded
c5	-15.9618719		-1.2301309874				Pb Pa	101325		''https://wmo.asu.edu/content/world-meteorological-organization-global-weather-climate-extremes-archive
c6	1.80122502		0.0147382054				Tb	288.15
							hb	0		Dhahran Saudi Arabia 8-Jul-2003 42^C and 35^C Dew Point approx RH 67%
			-8.3852031355				h	0		''https://en.wikipedia.org/wiki/Heat_index
ln(Pws)			3.9190845575
Pws	100		50.3543271805	'hPa - mb			Palt Pa	101325		56.7 Highest Temp Recorded
	54.8914267632		27.6402086264	'hPa - mb						''https://wmo.asu.edu/content/world-meteorological-organization-global-weather-climate-extremes-archive

Tn	273.16			-100	0.001								''http://www.1728.org/relhum.htm
Pn	6.11657													N=	0.6687451584
theta	1.1207717089											Dry Bulb
a0	-13.928169		-2.1895153707									T	33	ed=	50.3193642995
a1	34.707823		4.610288264				Pws & Pwi match the values in the tables					Wet Bulb
							of the following document :-					Tw	25.56	ew=	32.7427297689
			2.4207728933											RH=	54.89
ln(Pwi)			4.2317743752				''http://jlcinternational.com/measuring-humiditiy-basics/
Pwi	100		68.8392705648	'hPa - mb
	54.8914267632		37.7868577864	'hPa - mb

	A	m	Tn		Tmin	Tmax
Water	6.089613	7.33502	230.3921		0	200
Ice	6.114742	9.778707	273.1466		-70	0
					Page 6

		54.8914267632
Pws wat	50.5	27.7388105923
Pws ice	69.3	38.0140474968

	Heat Index
Heat Index	Lower Temp	Upper RH	Heat Index			''https://en.wikipedia.org/wiki/Heat_index
	Valid	Valid	37.6		Valid T >= 26.6 and RH >=40
Valid	Valid	Valid	39.1		Valid T = 21.1 – 46.1 and RH 0 – 80 if Heat Index < 65.6
	Valid		38.6		Appears to be Valid for T>=26.6 - Other Constraints Unknown
			38.1	←	Australian Apparent Temperature

			Heat Index							Compare Results with :-
			(Shade Values ^C)							''http://sugartech.co.za/psychro/
T	RH	T	27	32		Caution				''http://www.uigi.com/WebPsycH.html
^C	%	^F	32	41		Extreme Caution				''http://www.daytonashrae.org/psychrometrics_si.html#start
33	54.8914267632	91.4	41	54		Danger
			54			Extreme Danger

## Calc_2
Cells B1 – Q28 are for the calculations of Heat Indices
	''https://en.wikipedia.org/wiki/Heat_index

	Calculations for Heat Indices

	c1	-42.379	-42.4		c1	0.363445176	0.4		c1	16.923	16.9
	c2	2.04901523	187.3		c2	0.988622465	90.4		c2	0.185212	16.9
	c3	10.14333127	556.8		c3	4.777114035	262.2		c3	5.3941	296.1
	c4	-0.22475541	-1127.6		c4	-0.114037667	-572.1		c4	-0.100254	-503.0
	c5	-6.88E-003	-57.5		c5	-8.50E-004	-7.1		c5	9.42E-003	78.7
	c6	-5.48E-002	-165.2		c6	-2.07E-002	-62.4		c6	7.29E-003	22.0
	c7	1.23E-003	563.5		c7	6.88E-004	315.3		c7	3.45E-004	158.4
	c8	8.53E-004	234.9		c8	2.75E-004	75.7		c8	-8.15E-004	-224.4
	c9	-1.99E-006	-50.1		c9	0			c9	1.02E-005	257.0
	c10	0			c10	0			c10	-3.86E-005	-29.5
	c11	0			c11	0			c11	2.92E-005	4.8
	c12	0			c12	0			c12	1.43E-006	59.8
	c13	0			c13	0			c13	1.97E-007	3.0
	c14	0			c14	0			c14	-2.18E-008	-50.3
	c15	0			c15	0			c15	8.43E-010	1.2
	c16	0			c16	0			c16	-4.82E-011	-6.1
		^C	^F			^C	^F			^C	^F
	Heat Index	37.6	100		Heat Index	39.1	102		Heat Index	38.6	101
	Actual T^C	33	91.4		Actual T^C	33	91.4		Actual T^C	33	91.4

					# # # The End # # #